# International Plumbing Code

Section 715.1 (Sewage backflow Preventers).

Where the flood level rims of plumbing

fixtures are below the elevation of the manhole cover of the

next upstream manhole in the public sewer, such fixtures shall

be protected by a backwater valve installed in the building

drain, branch of the building drain or horizontal branch serving

such fixtures. Plumbing fixtures having flood level rims above

the elevation of the manhole cover of the next upstream manhole

in the public sewer shall not discharge through a backwater

valve.